## Slide 1: SCT/Pixel Draft Rack Layout 02-10-18 rcj
Draft Sub Rack Configuration
Gilbert we would appreciate your help in selecting the crates, fan tray and power supply. You will find attached a two page description of our crates with relevant information.
Concerns:
The power supply is not one of the selected options. It has been modeled after the prototype crates we have from Wiener. The location of the power supply is above the crate. This has been done to maximize the area available for optical cables and connectors. We fell strongly that the back of the crate should be open to minimize the potential of optical fiber damage. The replacement of defective back of the crate cards is also of much concern.
The dimensions of the sub rack is not clear from the documentation that we have been able to find. It would be helpful to have you fill in the dimensions (see red text).on page 2.
Please state the Wiener parts number that you would recommend (see page two red text).
The optical cable routing needs clarification. Please advise us as to the best contact to resolve this issues. We want to negotiate and come to a lasting agreements.
COMMENTS from G.Dumont:
To mount the Power Supply in front of the rack you need a Power Box not included in the CERN contract. The transparency for the air of the power supply is not very good but it would be sufficient because the low power in the BIN 9U (less than 1kW)
9U Power Supply variant 2, Pout 1900W, +5V/200A, +3.3V/200A , +/-12V/10A, 5 Power Modules, CANbus, Part No: OP06-1125 Power Box for P.S. variant 2 to be added, Part No: to be confirmed 9U BIN ( Subrack) with VME64x backplane variant 1 with 4 slots 6U Part No:OB06-011J 9U Fan Tray for 400mm modules and 220mm transition modules, 9 blowers with CANbus remote control Part No: OF00-070B
You will find in page two some requested dimensions

## Slide 2: SCT/Pixel Draft Rack Layout 02-10-18 rcj
400mm by 9U Cards
900W total
220 mm by 9U cards
550W
total
Power Supply 600W
Fan Tray
Heat Exchanger
Air Flow
9U
16 RODs
1 TIM
6U 1 CPU
Air Cooled
Power Supply
Round power pins with CANbus
Rack mounting
Part # OP06-1125
Power Box to be added
Part# ?????
Power
Connections
Fan tray with
CANbus
Covers full crate depth
Part # OF00-070B
Crate
1U space for round power pins
9U cards slots 5-21
Divider slot 4
6U cards slots 1-3
Part # OB06-011J
9U
16 BOC
Heat exchanger
Covers full crate depth
BIN 726 mm
3/4 U, 130/177 mm
10 U, 445mm
2 U, 89 mm
1 or 2 U, 44/88 mm
Sub Rack Configuration
Front of Rack Back of Rack
Slot utilization
1 CPU 6U Blank
2 Spare 6U Blank
3 Spare 6U Blank
4 6U to 9U Divide Blank
5 ROD 9U BOC 9U
6 ROD 9U BOC 9U
7 ROD 9U BOC 9U
8 ROD 9U BOC 9U
9 ROD 9U BOC 9U
10 ROD 9U BOC 9U
11 ROD 9U BOC 9U
12 ROD 9U BOC 9U
13 TIM 9U Blank
14 ROD 9U BOC 9U
15 ROD 9U BOC 9U
16 ROD 9U BOC 9U
17 ROD 9U BOC 9U
18 ROD 9U BOC 9U
19 ROD 9U BOC 9U
20 ROD 9U BOC 9U
21 ROD 9U BOC 9U
ROD Read Out Driver
BOC Back of Crate
(Optical interface and
s-link module)
TIM Timing Interface Module
(Interface to timing and L1 triggers)
P3 custom backplane used
Power Supply 3U /1300mm
Power Box 4U/177mm)
Power Box 457mm Power Supply 345mm

## Slide 3: SCT/Pixel Draft Rack Layout 02-10-18 rcj
4 of 16 cable
runs to the
BOC shown
Rear view of the crate
Cables are run along the sides of the crates. These cables will be in the same area used by utilities. Exact rules are to be determined
Side View of Rack
8x12 fiber link data per BOC. Radius of curvature greater than 6 cm desired
4x12 fiber control and 1 S_link cables per BOC. Radius of curvature greater than 6 cm desired
Curve is used to store up to 4 meters of cable. Uncertainty in cable length.
Cables are supported by bars near the back of crate.
Removable cover plate for back of crate.
Removal of plate turns of laser diode power.
Up to 16 data fiber cables per crates with up to 8x 12 fibers ribbons per cable. Radius of curvature of cables greater than 10 cm.
Up to 8 control fiber cables per crate with up to 8x12 fibers ribbons per cable. Radius of curvature greater than 10 cm is desired.
Power Utilization
+5 +3.3 + 12 - 12 Watts
One of 16 ROD 6A 4A 0 0 44W x16=704W
One or 16 BOC 2A 7A ~0A 0 33W x16=528W
One of 1 TIM 15A 8A 1.5A 1.5A 137W x1= 137W
One of 1 CPU 8A ~0A ~0A ~0A 40W x 1 = 40W
Total 151A 176A 1.5A 1.5A 1409W
Total front crate power 881W
Total back crate power 528W DC power of power modules: +5V/200A, +3.3V/200A, +/-12V/10A Total Power Supply: 1900W
400mm by 9U Cards
220 mm by 9U cards
Power Supply
Fan Tray
Heat Exchanger
400mm by 9U Cards
220 mm by 9U cards
Power Supply
Fan Tray
Heat Exchanger